PETROL FILLING STATIONS

SITE DECOMMISSIONING

These notes are intended to give guidance on decommissioning a petrol station. Please use the contact details at the foot of the page for further advice.

Partial or Full Site Closure

Tanks and pipework that have been used to store and dispense petrol remain a

hazard until such time that appropriate steps have been taken to remove the danger.

When it is necessary to close down some or all of the storage tanks on a petrol filling station on a temporary or permanent basis, the licensee, or where a licensed has lapsed, the occupier of the premises is responsible for ensuring that the installation is made safe.

Under the terms of the Petroleum Consolidation Regulations the Local Authority should be notified that a closure is about to take place and whether the site will be closed on a permanent or temporary basis.

In addition to that you may then be directed to do to make the site safe by an

inspector appointed by the Petroleum Enforcement Authority, the Civic Government

(Scotland) Act 1982 also permits the Local Authority to require that the site owner

makes safe any disused petrol tanks. Failure to address these issues can result in

enforcement action being taken and/or, the necessary work being undertaken by

the Local Authority and the cost being recovered from the site owner.

All work associated with making an installation safe should be carried out by

contractors working to a Safety Method Statement and, in cases involving such.

operations as removal of tank lids and entry into a tank, a Permit to Work. This is a

specialist job and should only be undertaken by contractors who are able to

demonstrate that they are competent to do so.

Detailed guidance is contained in the “Blue Book current addition”, which has been adopted by the Petroleum Enforcement Authority as their requirements for the design, construction and maintenance of petrol filling stations. The following guidance however provides a brief summary of these requirements.

It should be noted that the removal of all waste products from the site must be done in accordance with current legal requirements. Waste products in this context include any petrol, diesel, other fuel oils and any water present in the tanks or introduced into the tank and pipeline system during the decommissioning process. Site operators should consult with the Scottish Environment Protection Agency (SEPA) and/or Scottish Water in relation to their disposal of any such waste products.

Permanent Decommissioning

Following closure, a site may remain dormant for a considerable time prior to sale or redevelopment. Decommissioning should take place as soon as possible after the site has ceased trading.

The following measures should be carried out:

- Carry out a risk assessment taking into account all matters relating to health and safety and environmental considerations:

- The tanks made safe, together with the corresponding pipework either by removal from site or in situ:

- The dispensers removed and the electrical installation disconnected:

- The separator/interceptor cleaned.

Tanks

Pipework containing residual petrol should be drained back to the tank and flushed through with water prior to the removal of the product remaining in the tank.

Tanks being excavated.

When the tanks have been emptied and bottomed out either of the following 2 routes should be followed prior to excavation and removal from site: -

Route 1. Fill with either water, hydrophobic foam or nitrogen foam.

Or

Route 2. Fill with Nitrogen gas or dry ice or combustion gas or Clean and gas free, then check that oxygen level is below 5%.

Before removal from the site, all openings to excavated tanks should be sealed,

including apertures caused by corrosion. The label “Petrol Highly Flammable” should

be painted conspicuously on each side, or both ends, of the tanks.

The contractors responsible for removal of the tanks from the site must ensure that whoever receives them must be made aware of the previous use of the tanks and take the necessary health and safety precautions regarding toxicity and fire and

explosion hazards.

Whether the action is taken on the site is of a temporary or permanent nature the Petroleum enforcement authority will require to see documentary evidence that the work has been undertaken to recognised standards by competent contractors.

Tanks remaining in situ.

(This is not recommended for double skinned tanks)

Once the residual product has been removed one of the following methods may be used

- filling with hydrophobic foam

- filling with cement slurry having first been made inert by degassing.

- filling with foamed concrete

- converting to the storage of an alternative high flash product2

Pipework

Once cleaned with water all pipework should be removed from site. If removal is not possible the supply pipework should be disconnected from the tanks and the dispensers, and all apertures securely capped off.

Offset fills and vent pipes should also be disconnected and securely capped off.

Dispensers

Dispensers should be drained of petrol, purged with nitrogen and the suction line.

entry point plugged off before removal from the site.

Temporary Decommissioning

On occasions it may be necessary to “mothball” a site prior to redevelopment or sale to another operator. This will only be permitted for a limited time, normally not.

exceeding 12 months or as agreed with the Petroleum Enforcement Authority.

The Petroleum Enforcement Authority may only permit such temporary decommissioning where the site remains under a petroleum storage certificate, and they are satisfied that the site will continue to be adequately supervised.

In all cases of either temporary or permanent decommissioning, it is essential that the Petroleum Enforcement Authority is consulted and kept informed as the work progresses.

Contaminated Land Issues

It is recommended that you seek advice from the Dumfries and Galloway Council Contaminated Land Team regarding any redevelopment of formerly licensed petrol filling stations and fuel storage facilities.

If the site were to be subject of a planning application the site owners would be required to demonstrate that the land is ‘suitable for use’ as per Planning Advice Note (PAN) 33 (2000). The requirements will vary according to the future use of the site and the condition of the site.

If the there is a change of use to a more sensitive category (for example residential), a site investigation will be required. If the planning application does not involve excavations or a change of use to a more sensitive category (for example using only existing buildings for a commercial use) a site investigation may not be required. However if there is evidence of residual contamination affecting the ground or a watercourse, remediation may be required under Part 2A of the Environmental Protection Act 19 90, regardless of the future use of the site.

Further information and guidance can be obtained from: -

Trading Standards

Tradingstandards@dumgal.gov.uk

Contaminated Land

ContaminatedLand@dumgal.gov.uk

1 Guidance for the Design, Construction and Maintenance of Petrol Filling Stations” published jointly by the Energy Institute and the Association of Petroleum and Explosives Administration; ISBN 0 85293 419ZX +44(0) 1206 796 351  https://apea.org.uk/

2 This option is only applicable to cases where the tanks are proven to be free of leaks and where on the basis of a risk assessment it has been expressly agreed with the Petroleum Enforcement Authority.